### Chapter 17:  Development of Exit Strategies for Responders

### Providing Restoration Assistance through the FlaWARN Network

The purpose of the Florida Water and Wastewater Agency Response Network (FlaWARN) is the timely restoration of essential water and wastewater service to impacted populations. Generally, these response activities are intended to be short-term. In most cases restoration will consist of restoring temporary power and making the repairs necessary to render facility equipment operational.

### Requirements for the Use of Prudent Response Procedures

In an effort to protect public health and the environment, assisting utilities will use prudent response procedures to restore essential potable water and wastewater functions.  Further, efforts will be made to restore equipment at water plants, wastewater plants, and assure water quality and quantity.  These repairs should be completed using many of the BMP’s described in this document.  In some cases unconventional repairs may be necessary to restore service quickly pending more permanent repairs.  The purpose of a responder is to restore service in a safe and reliable manner, as soon as possible and/or to protect the environment from contamination.  Longer-term reconstruction and repairs to the water and wastewater systems are the responsibility of the damaged utility. In the long-term, the damaged utility should secure the contractors, equipment, materials, etc., necessary to return the system to its normal condition.

### Considerations for Responder Utility Personnel

In an effort to restore service in a timely manner, the assisting utilities may be expected to arrive ASAP. In an attempt to restore service efficiently and effectively, they may be expected to work long hours and extended workweeks under very adverse eating and sleeping conditions.  For longer-term responses, work crews may need to be rotated in and out of the damaged area to keep workers alert, productive, and safe. An additional priority is getting the assisting utility workers back home where their normal workload is being performed by other utility employees, and to their families who may have needs of paramount importance.

### Completion of Restoration Activities and Exit of Responder Agency

Once water service (including quality, pressure and quantity) along with wastewater service (including collection, pumping, treatment and disposal) can be confirmed, the damaged utility has the obligation to maintain the operation. Response activities are not normally intended to provide long-term replacements for utility employees, unless there is an agreement and/or a demonstrated need to do so. Before departing, the responding crews should make arrangements with the assisted utility for fueling, lubrication, and standard equipment checks. Also necessary are provisions for safekeeping of equipment when it is no longer needed and agreements beforehand on whether the equipment can be moved by the damaged utility to other locations. When these arrangements are made, the responding utility can return home.

### Determining the End Point of Responder Assistance

It can be difficult to judge when a responder utility’s work is finished. The most obvious measure is when power has been restored to the impacted facility. Once power is restored it is imperative that temporarily loaned equipment be disconnected and moved to areas where power may still be lacking or returned back to the lending agency. Restoration of power is indicative of a condition where permanent repairs to equipment can be initiated by the damaged utility.

Reconstruction work requests are a frequent issue and it was not the intent of FlaWARN to assist damaged utilities with these needs.  Normally, the assisting utility will not remain at the damaged utility to do reconstruction, long-term repairs and recovery, or infrastructure installation. These types of long-term improvement responsibilities were not contemplated as part of the Mutual Aid Agreement and are better handled by private contractors who are licensed to do this kind of work.

For example if a damaged utility asks the assisting utility to install two and a half miles of water main to improve water service in an area of the community, this is a clear signal that the response phase has ended and the repair and reliability improvement phase had begun.  It is best if the crew leaders from both damaged and assisting utilities communicate early and often in the response process as to restoration goals, including what has been achieved and what remains to complete the response. The goal should always be to place the system in a condition where the damaged utility can manage it.

It should be noted that rarely do the responders or responding utility crews ask to go home or leave the damaged utility.  In less than one day, the responders may become fully invested, attached, and committed to the response effort.  Because of the dire situation, the responding workers are going to work as hard as they would or harder than they do at their own system.  They naturally want to stay and alleviate any suffering they can for the damaged utility and community. It is also natural that damaged utilities will want to keep good responders around as long as possible, once their abilities have been demonstrated.

When an assisting utility returns home the damaged utility may still need equipment, like generators and by-pass pumps.  If the assisting utility is willing to leave behind any equipment the BMPs on loaning equipment should be followed.

Besides operating, maintaining, repairing, and safeguarding the equipment, the damaged utility should coordinate with the assisting utility to return the equipment and any accessories ASAP, in at least as good condition as it was received.  If the equipment can be spared until operations return to normal at the damaged utility location, it is appropriate that the damaged utility return the equipment to the assisting utility instead of relying on the lending utility to come get it or make arrangements for its return.

When transporting equipment to the home location, the assisting utility should check all vehicles, trailers, tires, rigging, and equipment to ensure security, safety and proper working condition for the return trip home.  Also, remember the need to accommodate what will likely be a very tired crew.  The returning crews may need to be reminded to take great care when returning home, make frequent stops and driver rotations, and secure lodging if needed to prevent potential accidents and unnecessary risk from fatigue. At all times CDL regulations and posted traffic speeds should be adhered to, so as not to endanger the public.

### Need for Debriefing of Responder Personnel

Once the assisting utility returns and the responders are rested, a debriefing meeting should be held to share experiences and insights to benefit future responders. The debriefing aids the assisting utility, helping them analyze and improve their Emergency Preparedness and Response Plan. Every response opportunity will provide learning experiences that can be used to increase effective operations at home and in the field.

### A1: Weather/Hurricane Terms and Acronyms

(Retrieved 4/7/06 from: http://www-nmcp.med.navy.mil/newsweath/terms.asp)

| ARWO | Aerial Reconnaissance Weather |
| --- | --- |
| AFOS | Automation of Field Operations and Services |
| ASOS | Automated Surface Observing Systems |
| AWIPS | Advanced Weather Interactive Processing System |
| AOC | Army Operations Center, Pentagon |
| ARC | American Red Cross |
| ARES | Amateur Radio Emergency Services |
| ARRL | American Radio Relay League |
| CARCAH | Chief, Aerial Reconnaissance Coordination, All Hurricanes |
| CONUS | Continental United States |
| DAE | Disaster Assistance Employee |
| DAC | Disaster Application Center |
| DCO | Defense Coordinating Officer |
| DFO | Disaster Field Office |
| DOC | Department of Commerce |
| EAS | Emergency Alert System |
| EBS | Emergency Broadcast System |
| EICC | Emergency Information and Coordination Center (FEMA) |
| EMS | Emergency Medical Services |
| EMWIN | Emergency Manager's Weather Information Center |
| EOC | Emergency Operations Center |
| EOP | Emergency Operations Plan |
| ERT | Emergency Response Team (FEMA) |
| ERT-A | Advance Element of the Emergency Response Team (FEMA) |
| ESF | Emergency Support Function |
| EST | Emergency Support Team (FEMA) |
| FAST | Field Assessment Team |
| FCO | Federal Coordinating Officer (FEMA) |
| FEMA | Federal Emergency Management Agency |
| FRP | Federal Response Plan |
| GMT | Greenwich Mean Time |
| GOES | Geostationary Operational Environmental Satellite |
| HES | Hurricane Evacuation Study |
| HF | High Frequency |
| ICS | Incident Command System |
| IT | Information Technology Directorate (FEMA) |
| KM | Kilometers |
| JIC | Joint Information Center |
| M | Statute Mile |
| MB | Millibars |
| MEOW | Maximum Envelope of Water or Maximum Envelope of Winds |
| MERS | Mobile Emergency Response Support (FEMA) |
| MPH | Miles Per Hour |
| MOC | MERS Operations Center (FEMA) |
| M/S | Meters Per Second |
| MT | Mitigation Directorate (FEMA) |
| NASA | National Aeronautics and Space Administration |
| NAWAS | National Warning System |
| NDMS | National Disaster Medical System |
| NECC | National Emergency Coordination Center (FEMA) |
| NEXRAD | Next Generation of Radar |
| NHC | National Hurricane Center |
| NM | Nautical Mile |
| NPSC | National Process Serving Center (FEMA) |
| NTC | National Teleregistration Center (FEMA) |
| NOAA | National Oceanic and Atmospheric Administration |
| NVOAD | National Voluntary Organizations Active in Disaster |
| NWS | National Weather Service |
| NWSFO | National Weather Service Forecasting Office |
| OSC | On-Scene Coordinator |
| OS | Operations Support Directorate (FEMA) |
| PIO | Public Information Officer |
| PT | Preparedness, Training and Exercises Directorate (FEMA) |
| PUP | Principle User Processor |
| RACES | Radio Amateur Civil Emergency Service |
| RADAR | Radio Detection And Ranging |
| RD | Regional Director |
| REACT | Radio Emergency Associated Communication Team |
| ROC | Regional Operations Center |
| RR | Response and Recovery Directorate (FEMA) |
| SCO | State Coordinating Officer |
| SITREP | Situation Report |
| SLOSH | Sea, Lake, and Overland Surges for Hurricanes |
| SOP | Standard Operating Procedure |
| TD | Tropical Depression |
| TS | Tropical Storm |
| TPC | Tropical Prediction Center |
| TAFB | Tropical Analysis and Forecast Branch (TPC) |
| TSB | Technical Support Branch (TPC) |
| USACE | United States Army Corps of Engineers |
| USAF | United States Air Force |
| USCG | United States Coast Guard |
| USGS | United States Geological Survey |
| USN | United States Navy |
| USAR | Urban Search and Rescue |
| UTC | Universal Time Coordinate |
| WFO | Weather Forecast Office |
| Z | Zulu Time |

### A2: Glossary & Related Links

The US-EPA provides a thorough list of water security and response related links at http://cfpub.epa.gov/safewater/watersecurity, including a glossary and the following:

A to Z Subject Index

- Bioterrorism Act

- Emergency / Incident Planning

- EPA Contacts

- EPA Environmental Laboratory Compendium

- Grants and Funding

- Information Sharing

- Legislation / Directives

- Office of Ground Water and Drinking Water

- Office of Water

- Publications

- Guidance

- Homeland Security Presidential Directives

- Outreach Materials

- Legislation

- Newsletters

- Reports and Studies

- Webcast Presentations

- Public Involvement

- Related Links

- Trade/Industry Organizations

- Clearinghouses and Information Centers

- Federal Government

- State Homeland Security Web Sites

- State Drinking Water Protection Web Sites

- EPA Program and Regional Offices

- Security Enhancements, Research and Technology

- Tools and Technical Assistance

- Training Courses, Meetings, and Workshops

- Vulnerability Assessments

- Water Information Sharing and Analysis Center (WaterISAC)

- Water Security Home

### A3: FlaWARN Water Security

### Abbreviation and Acronym List

| AAR | After Action Review |
| --- | --- |
| AC | Alternating current |
| ACL | Access control list |
| ACOE | Army Corps of Engineers |
| AMSA | Association of Metropolitan Sewerage Agencies |
| AMWA | Association of Metropolitan Water Agencies |
| AP | Action Plan |
| ASCE | American Society of Civil Engineers |
| ASDWA | Association of State Drinking Water Administrators |
| AWWA | American Water Works Association |
| AwwaRF | American Water Works Association Research Foundation |
| BACT | Best Available Control Technology |
| BOD | Biological Oxygen Demand |
| BWN | Boil Water Notice |
| Ca(OCl)2 | Calcium hypochlorite |
| CaO | Calcium oxide |
| CaOH2 | Calcium hydroxide |
| Ca(OCL)2 | Calcium hypochlorite |
| CBR | Chemical, biological, or radiological |
| CBRNE | Chemical, Biological, Radiological/Nuclear, and Explosive |
| CCC | Chlorine contact chamber (also, cross connection control) |
| CCP | Communication Cluster Phenomenon |
| CCTV | Closed-circuit television |
| CDC | Center for Disease Control |
| CFR | Code of Federal Regulations |
| CHIPS | Citizens Helping in Policy Service |
| CIP | Capital improvement plan |
| CMMS | Computerized maintenance management system |
| CPR | Cardio-pulmonary resuscitation |
| CPTED | Crime Prevention Through Environmental Design |
| CWS | Community Water System |
| DBT | Design basis threat |
| DEP | Department of Environmental Protection |
| DHS | Department of Homeland Security |
| DoD | Department of Defense |
| DoS | Department of State |
| EOC | Emergency Operations Center |
| EPA | United States Environmental Protection Agency |
| ERP | Emergency Response Plan |
| ERT | Environmental Response Team |
| ESF | Emergency Support Function |
| EWS | Early warning system |
| FBI | Federal Bureau of Investigation |
| FDEP | Florida Department of Environmental Protection |
| FEMA | Federal Emergency Management Agency |
| FlaWARN | Florida's Water/Wastewater Agency Response Network |
| FOIA | Freedom of Information Act |
| FRWA | Florida Rural Water Association |
| GASB | Government Accounting Standards Board |
| GETS | Government Emergency Telecommunications Service |
| GIS | Geographic information system |
| GPS | Geographic positioning system |
| GSA | General Services Administration |
| HAZMAT | Hazardous Materials |
| HAZWOPER | Hazardous Waste Operation and Emergency Response |
| HCl | Hydrochloric acid |
| HHS | Health and Human Services |
| HMI | Human machine interface |
| HSAS | Homeland Security Advisory System |
| HVAC | Heating, ventilation, and air conditioning |
| IAP | Incident Action Plan |
| IC | Incident Commander |
| ICS | Incident Command System |
| ID | Identification |
| IDS | Intrusion Detection System |
| IED | Improvised explosive device |
| IID | Improvised incendiary device |
| IP | Internet protocol |
| ISAC | Water Information Sharing and Analysis Center |
| JOC | Joint Operations Center (established by the FBI) |
| LEO | Law Enforcement Officer |
| LEPC | Local Emergency Planning Committees |
| LIMS | Laboratory Information Management System |
| LRN | Laboratory Resource Network |
| MHZ | Megahertz |
| MPEG | Moving Picture Experts Group |
| Na2CO3 | Soda ash |
| NaOCl | Sodium hypochlorite |
| NaOH | Sodium hydroxide |
| NFPA | National Fire Protection Association |
| NIC | NIMS Integration Center |
| NIMCAST | NIMS Capability Assessment Support Tool |
| NIMS | National Incident Management System |
| NIOSH | National Institute of Occupational Safety & Health |
| NRP | National Response Plan |
| NRWA | National Rural Water Association |
| O&M | Operations and maintenance |
| OSHA | Occupational Health and Safety Administration |
| PC | Personal computer |
| pH | A measure of the activity of hydrogen ions (H+) in a solution and, therefore, its acidity or alkalinity |
| PIO | Public Information Officer |
| PIR | Passive infrared |
| PLC | Programmable logic controller |
| ppb | Parts per billion |
| PPE | Personal protection equipment |
| PR | Press Release |
| PRV | Pressure reducing valves |
| PSN | Public switched network |
| RAM | Random access memory |
| RAM-D | Risk Assessment Methodology for Dams |
| RAM-WTM | Risk Assessment Methodology for Water Utilities |
| RFID | Radio frequency identification |
| RPG | Rocket propelled grenade |
| RPTB | Response Protocol Tool Box |
| RTU | Remote terminal unit |
| SCADA | Supervisory Control and Data Acquisition |
| SCBA | Self-contained breathing apparatus |
| SERT | State Emergency Response Team |
| SO | Sherriff's Office |
| SOP | Standard Operating Procedure |
| TLV | Total Threshold Value |
| TOC | Total Organic Carbon |
| TREEO | Training, Research and Education for Environmental Occupations |
| UC | Unified Command |
| UF | University of Florida |
| UL | Underwriters Laboratory |
| UPS | Uninterruptible power supply |
| VA | Vulnerability assessment |
| Vac | Volts alternating current |
| Vdc | Volts direct current |
| VOCs | Volatile Organic Compounds |
| VSATTM | Vulnerability Self-Assessment Tool |
| WMD | Weapons of Mass Destruction |
| WTP | Water treatment plant |
| WWTP | Wastewater treatment plant |

### A4:  Florida Division of Emergency Management

### Florida’s Division of Emergency Management is responsible for preparing the state to respond to emergencies, recover from them, and mitigate their impacts. Bureaus include Compliance Planning & Support, Policy & Planning, Preparedness & Response, and Recovery & Mitigation.

www.floridadisaster.org is designed to support these objectives. This site provides information and planning tools to the Florida Emergency Management Community. This service is continually under development. We try to keep the information timely and accurate and will make every effort to correct errors brought to our attention.

The State Emergency Response Team (SERT) is set up to manage disasters through Emergency Operations Centers (EOC’s) set up affected counties in preparation and in the aftermath of a disaster.  The SERT mission is to ensure that Florida is prepared to respond to emergencies, recover from them, and mitigate against their impacts. The SERT Organizational Structure is shown below:

Hurricane Preparedness

The goal of the SERT Hurricane Preparedness Web site is to inform the public about the hurricane hazards and provide knowledge which can be used to take ACTION. This information can be used to save lives at work, home, while on the road, or on the water.

Up to date information on preparing and responding to hurricanes can be found at: www.nhc.noaa.gov/HAW2/english/intro.shtml

Florida Division of Emergency Management Online Mapping

Florida's Division of Emergency Management provides an Online Mapping service. The purpose of these maps is to provide the citizens of Florida with current and accurate information which can be used to prepare for and recover from disasters. There are two types of mapping sites, a plug-in required site and a non-plug-in site. The plug-in map will provide you with many functions, while the non-plug-in is limited yet still provides the necessary information you need in times of disaster.  Maps can be accessed at the interactive sites listed below:

Disaster Preparedness Maps

Interactive Florida Map
(*NEW* plug-in required, should auto-load) 
- Find Evacuation Routes and Zones, Storm Surge Information, and Open Shelter Locations. (*Need MS Windows XP, 2000, 98 SE, NT 4.0- MS Internet Explorer 5.x, need administrative rights to install*)

Other Mapping Sites

Hazard Maps - www.HazardMaps.gov

Terra Fly - Aerial Imagery

TAOS - Storm Hazard Model Outputs

USGS GEODE - Geo-Data Explorer

NOAA Fire Detection

US Forestry Service Fire Detection

Additional information can be obtained from the Florida Division of Emergency Management at the noted WEB sites.

### A5:  FlaWARN Mutual Aid Agreement

MUTUAL AID AGREEMENT FOR WATER/WASTEWATER

ARTICLE I. PURPOSE

The Water/Wastewater Mutual Aid Program was established to provide a method whereby water/wastewater utilities sustaining physical damage from natural or man made disasters could obtain emergency assistance, in the form of personnel, equipment, and materials and other associated services necessary, from other water/wastewater utilities. The purpose of this Agreement is to formally document such program.

ARTICLE II. DEFINITIONS

A. AGREEMENT – The Water/Wastewater Mutual Aid Agreement. The original agreement and all signatory pages shall be kept at TREEO Center 3900 SW 63rd Blvd., Gainesville, FL 32608

B. PARTICIPATING UTILITY – Any Water/Wastewater utility which executes this Mutual Aid Agreement.

C. DAMAGED UTILITY – Any Participating Utility which sustains physical damage to its water/ wastewater system due to a natural or manmade disaster and seeks assistance pursuant to this Agreement.

D. ASSISTING UTILITY – Any Participating Utility which agrees to provide assistance to a Damaged Utility pursuant to this Agreement.

E. AUTHORIZED REPRESENTATIVE – An employee of a Participating Utility authorized by that utility’s governing board to request or offer assistance under the terms of this Agreement. (A list of the Authorized Representatives for each Participating Utility shall be attached to this Agreement as Appendix A)

F. PERIOD OF ASSISTANCE – The period of time beginning with the departure of any personnel of the Assisting Utility from any point for the purpose of traveling to the Damaged Utility in order to provide assistance and ending upon the return of all personnel of the Assisting Utility, after providing the assistance requested, to their residence or place of Work, whichever is first to occur.

G. SCHEDULE OF EQUIPMENT RATES – The latest rates published by Federal Emergency Management Agency under the response and recovery directorate applicable to major disasters and emergencies.

H. WORK OR WORK-RELATED PERIOD – Any period of time in which either the personnel or equipment of the Assisting Utility are being used by the Damaged Utility to provide assistance. Specifically included within such period of time are rest breaks when the personnel of the Assisting Utility will return to active Work within a reasonable time. Also, included is mutually agreed upon rotation of personnel and equipment.

ARTICLE III. PROCEDURE

In the event that a particular utility becomes a Damaged Utility, the following procedure shall be followed:

A. The Damaged Utility shall contact the Authorized Representative of one or more of the participating utilities and provide them with the following information:

1. 	a general description of the damage sustained;

2. 	the part of the water/wastewater system for which assistance is needed;

3. 	the amount and type of personnel, equipment, materials and supplies needed and a reasonable estimate of the length of time they will be needed;

4. 	the present weather conditions and the forecast for the next twenty-four hours; and

5. 	a specific time and place for a representative of the Damaged Utility to meet the personnel and equipment of the Assisting Utility.

6. 	The identification of Work conditions and special constraints such as availability of fuel supplies, lodging/meal support, medical facilities, security, communications, etc.

B. When contacted by a Damaged Utility, the Authorized Representative of a Participating Utility shall assess his utility’s situation to determine whether it is capable of providing assistance. No Participating Utility shall be under any obligation to provide assistance to a Damaged Utility. If the Authorized Representative determines that the Assisting Utility is capable of and willing to provide assistance, the Assisting Utility shall so notify the Authorized

Representative of the Damaged Utility and providing the following information:

1. 	a complete description of the personnel, equipment and materials to be furnished to the Damaged Utility.

2. 	the estimated length of time the personnel, equipment and materials will be available;

3. 	the work experience and ability of the personnel and the capability of the equipment to be furnished;

4. 	the name of the person or persons to be designated as supervisory personnel; and

5. 	the estimated time when the assistance provided will arrive at the location designated by the Authorized Representative of the Damaged Utility.

C. The personnel and equipment of the Assisting Utility shall remain, at all times, under the direct supervision and control of the designated supervisory personnel of the Assisting Utility. In instances where only equipment is provided by the Assisting Utility, the ownership of said equipment shall remain with the Assisting Utility and said equipment shall be returned to the

Assisting Utility immediately upon request. Representatives of the Damaged Utility shall suggest Work assignments and schedules for the personnel of the Assisting Utility; however, the designated supervisory personnel of the Assisting Utility shall have the exclusive responsibility and authority for assigning Work and establishing Work schedules for the personnel of the

Assisting Utility. The designated supervisory personnel shall maintain daily personnel time records and a log of equipment hours, be responsible for the operation and maintenance of the equipment furnished by the Assisting Utility, and report Work progress to the Damaged Utility.

D. The Damaged Utility shall have the responsibility of providing food and housing for the personnel of the Assisting Utility from the time of departure from their regularly scheduled Work location until the time of return to their regularly scheduled Work location. The food and shelter provided shall be subject to the approval of the supervisory personnel of the Assisting Utility. If

not agreeable, food and shelter shall be provided and paid for as determined by mutual agreement.

E. The Damaged Utility shall have the responsibility of providing communications between the personnel of the Assisting Utility and the Damaged Utility.

ARTICLE IV. REIMBURSABLE EXPENSES

The terms and conditions governing reimbursement for any assistance provided under this Agreement shall be agreed to prior to the providing of such assistance and shall be in accordance with the following provisions:

A. PERSONNEL – During the Period of Assistance, the Assisting Utility shall continue to pay its employees according to its then prevailing rules and regulations. The Damaged Utility shall reimburse the Assisting Utility for all direct and indirect payroll costs and expenses incurred during the Period of Assistance, including, but not limited to, employee pensions and benefits.

B. EQUIPMENT – The Assisting Utility shall be reimbursed for the use of its equipment during the Period of Assistance according to the SCHEDULE OF EQUIPMENT RATES established and published by FEMA. If an Assisting Utility uses an alternate basis of rates for equipment listed on the FEMA Schedule of Equipment Rates it shall provide such rates to the Damaged

Utility prior to providing assistance. Rates for equipment not referenced on the FEMA Schedule of Equipment Rates shall be developed based on actual recovery of costs.

C. MATERIALS AND SUPPLIES – The Assisting Utility shall be reimbursed for all materials and supplies furnished by it and used or damaged during the Period of Assistance, unless such damage is caused by negligence of the Assisting Utility’s personnel. The measure of reimbursement shall be the replacement cost of the materials and supplies used or damaged, plus

ten (10) percent of such cost. In the alternative, the parties may agree that the Damaged Utility will replace, with a like kind and quality as determined by the Assisting Utility, the materials and supplies used or damaged.

D. PAYMENT – Unless mutually agreed otherwise, the Assisting Utility should bill the requesting utility for all expenses not later than ninety (90) days following the Period of Assistance. The requesting utility shall pay the bill in full not later than forty-five (45) days following the billing date. Unpaid bills shall become delinquent upon the forty-fifth (45th) day following the billing date, and once delinquent shall accrue interest at the rate of prime plus two percent (2percent) per annum as reported by the Wall Street Journal.

E. DISPUTED BILLINGS – Those undisputed portions of a billing should be paid under this payment plan. Only the disputed portions should be sent to arbitration under Article VI.

ARTICLE V. INSURANCE

Each Participating Utility shall bear the risk of its own actions, as it does with its day-to-day operations, and determine for itself what kinds of insurance, and in what amounts, it should carry. Nothing herein shall act or be construed as a waiver of any sovereign immunity or other exemption or limitation on liability that a Participating Utility may enjoy.

ARTICLE VI. ARBITRATION

All disputes between two or more participating utilities arising from participation in this Agreement, which cannot be settled through negotiation, shall be submitted to binding arbitration before a panel of three persons chosen from the members of this Mutual Aid Agreement which are participating utilities, excluding those members that are parties to the dispute.

Each party to the dispute shall choose one panel member and those panel members shall agree on one additional panel member. The panel shall adopt rules of procedure and evidence, shall determine all issues in dispute by majority vote and shall assess damages. The decision of the panel shall be final and binding upon the parties to the dispute.

NOW, THEREFORE, in consideration of the covenants and obligations contained herein, the participating utility listed here, as a Participating Utility duly executes this Water/ Wastewater Mutual Aid Agreement this ________ day of _____________, 20 __ .

Water/Wastewater Utility Representative(s):

By:______________________

Title:_____________________

____________________________________

Please Print Name

By: ______________________

Title: _____________________

______________________________________

Please Print Name

Name of Participating Utility: ____________________________

Please Print Name of Utility

(Please note: Attach a copy of your FlaWARN registration form to this document when you submit it. Thank you.)

| WATER UTILITY COMAPNY - CHARGE SUMMARY Charge Summary for Work Performed ### A6: Work Management Documentation |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CITY OF RECOVERY, FL RELIEF MISSION |  |  |  |  |  |  |  |  |  |  |  |  |  |
| PERSONNEL EXPENSE |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | NAME |  | REGULAR |  | BENEFIT | BENEFIT |  | OVERTIME |  | OT BENEFIT | BENEFIT |  | TOTAL |
| POSITION | LAST | FIRST | AMOUNT |  | RATE | COST |  | AMOUNT |  | RATE | COST |  | CHARGE |
| ELECTRICIAN/INSTRUMENTATION TECHNICIAN | EMPLOYEE 1 | A. | $1,543.04 |  | 48.92percent | $754.86 |  | $3,226.50 |  | 13.35percent | $430.74 |  | $5,955.13 |
| SYSTEM MECHANIC | EMPLOYEE 2 | B. | $1,241.60 |  | 48.92percent | $607.39 |  | $2,538.00 |  | 13.35percent | $338.82 |  | $4,725.81 |
| UTILITY TECH I | EMPLOYEE 3 | C. | $1,041.60 |  | 48.92percent | $509.55 |  | $1,743.55 |  | 13.35percent | $232.76 |  | $3,527.46 |
| SENIOR UTILITY TECH I | EMPLOYEE 4 | D. | $1,328.80 |  | 48.92percent | $650.05 |  | $2,275.38 |  | 13.35percent | $303.76 |  | $4,557.99 |
| SYSTEM MECHANIC ASSISTANT | EMPLOYEE 5 | E. | $822.40 |  | 48.92percent | $402.32 |  | $1,681.23 |  | 13.35percent | $224.44 |  | $3,130.39 |
| SENIOR UTILITY TECH I | EMPLOYEE 6 | F. | $1,148.00 |  | 48.92percent | $561.60 |  | $1,965.00 |  | 13.35percent | $262.33 |  | $3,936.93 |
| SYSTEM MECHANIC ASSISTANT | EMPLOYEE 7 | G. | $822.40 |  | 48.92percent | $402.32 |  | $1,719.78 |  | 13.35percent | $229.59 |  | $3,174.09 |
| UTILITY TECH I | EMPLOYEE 8 | H. | $931.20 |  | 48.92percent | $455.54 |  | $1,563.35 |  | 13.35percent | $208.71 |  | $3,158.80 |
| 1. PERSONNEL TOTAL |  |  | $8,879.04 |  |  | $4,343.63 |  | $16,712.79 |  |  | $2,231.16 |  | $32,166.61 |
| OTHER BILLABLE EXPENSES |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. VEHICLE USE |  |  |  |  |  |  |  | IMPORTANT NOTE: It is essential that you provide documentation of specific utility pay policies that provide basis for calculations such as definition of overtime, overtime pay if different from standard time and a half, etc. |  |  |  |  |  |
|  |  |  | VEHICLE |  |  |  |  |  |  |  |  |  |  |
| TYPE | MILES | RATE* | AMOUNT |  |  |  |  |  |  |  |  |  |  |
| Vehicle# WS218 - 2000 F-350 Ford Truck |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROUND TRIP MILES (547 EA Way) | 1,094 | $0.45 | $492.30 |  |  |  |  |  |  |  |  |  |  |
| MOSS POINT MILES(12 Days) | 360 | $0.45 | $162.00 |  |  |  |  |  |  |  |  |  |  |
| Vehicle# WS278 - 2003 GMC Sierra 3500 Truck |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROUND TRIP MILES (547 EA Way) | 1,094 | $0.45 | $492.30 |  |  |  |  |  |  |  |  |  |  |
| MOSS POINT MILES(12 Days) | 360 | $0.45 | $162.00 |  |  |  |  |  |  |  |  |  |  |
| Vehicle# WS327 - 2004 Chevy Silverado 3500 Truck |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROUND TRIP MILES (547 EA Way) | 1,094 | $0.45 | $492.30 |  |  |  |  |  |  |  |  |  |  |
| MOSS POINT MILES(12 Days) | 360 | $0.45 | $162.00 |  |  |  |  |  |  |  |  |  |  |
|  | 4,362 |  | $1,962.90 |  | TOTAL VEHICLE COST |  |  |  |  |  |  |  |  |
| *FEMA AUTHORIZED RATE |  |  |  |  |  |  |  |  | TOTAL COST |  |  |  |  |
| 3. MEALS |  |  |  |  |  |  |  |  |  | PERSONNEL |  |  | $32,166.61 |
|  |  |  | MEAL |  |  |  |  |  |  | VEHICLE |  |  | $1,962.90 |
| PLACE |  |  | AMOUNT |  |  |  |  |  |  | MEALS |  |  | $1,140.26 |
|  |  |  |  |  |  |  |  |  |  | LODGING |  |  | $1,238.72 |
| See Attached Detail |  |  | $1,140.26 |  | TOTAL MEALS |  |  |  |  | OTHER SUPPLIES |  |  | $3,099.69 |
| 4. LODGING |  |  |  |  |  |  |  |  |  | GRAND TOTAL |  |  | $39,608.18 |
|  |  |  | LODGING |  |  |  |  |  |  |  |  |  |  |
| PLACE |  |  | AMOUNT |  |  |  |  |  |  |  |  |  |  |
| Edison Wathall Hotel |  |  | $1,238.72 |  | TOTAL LODGING |  |  |  |  |  |  |  |  |
| 5. OTHER REQUIRED SUPPLIES |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | OTHER |  |  |  |  |  |  |  |  |  |  |
| ITEMS |  |  | AMOUNT |  |  |  |  |  |  |  |  |  |  |
| See Attached Detail |  |  | $3,099.69 |  | TOTAL OTHER |  |  |  |  |  |  |  |  |

| YOUR COMPANY LOGO |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| YOUR COMPANY NAME |  |  |  |  |  | Date: | 10/01/20XX |  |
|  |  |  |  |  |  | Invoice #: | XXXXXX |  |
| 123 Main Street |  |  |  |  |  |  |  |  |
| Assisting Utility, FL 12345-0000 |  |  |  |  |  |  |  |  |
| Ph: | (123) 456-7890 |  |  |  |  |  |  |  |
| Fax: | (123) 456-7891 |  |  |  |  |  |  |  |
| Bill To |  |  |  | Copy To |  |  |  |  |
| CITY OF RECOVERY |  |  |  | FLAWARN HQ |  |  |  |  |
| 123 Main Street |  |  |  | UF/TREEO Center |  |  |  |  |
| Recovery, FL 12345-0000 |  |  |  | 3900 SW 63rd Blvd |  |  |  |  |
|  |  |  |  | Gainesville, FL 32608 |  |  |  |  |
| Ph: | (987) 654-3210 |  |  |  |  |  |  |  |
| Item | Meter # | Description |  | Unit | Quantity |  | Unit Price | Amount |
| 1 |  | Katrina FlaWARN Responder |  |  |  |  |  |  |
|  |  | To: City of Recovery, FL |  |  |  |  |  |  |
|  |  | SERT Mission #999 |  |  |  |  |  |  |
|  |  | 8 Employees for 12 days |  |  |  |  |  | $32,166.61 |
|  |  | Sept 3rd - Sept 14th, 20XX |  |  |  |  |  |  |
|  |  | Vehicle expense |  |  |  |  |  | $1,962.90 |
|  |  | Meal expense |  |  |  |  |  | $1,140.26 |
|  |  | Lodging expense |  |  |  |  |  | $1,238.72 |
|  |  | Other required supplies |  |  |  |  |  | $3,099.69 |
|  |  | Please see attached summary |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  | Total Amount | $39,608.18 |
|  |  |  |  | Rate |  |  | Tax |  |
|  |  |  |  |  |  |  | Shipping |  |
|  |  |  |  |  |  |  | Total Invoice | $39,608.18 |
|  |  |  |  |  |  |  | Payment |  |
|  |  |  |  |  |  |  | Balance Due | $39,608.18 |
| Message |  |  |  |  |  |  |  |  |

# Work Management Document

| WATER UTILITY COMPANY |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SCHEDULE OF FRINGE BENEFIT CALCULATIONS |  |  |  |  |  |  |  |
|  |  |  | REGULAR |  | OVERTIME |  |  |
| BENEFIT COMPONENTS |  |  | PAY |  | PAY |  |  |
| SICK PAY |  |  | 4.80percent |  | 0.00percent |  |  |
| VACATION |  |  | 6.00percent |  | 0.00percent |  |  |
| WORKER'S COMP |  |  | 5.70percent |  | 5.70percent |  |  |
| INSURANCES |  |  | 11.70percent |  | 0.00percent |  |  |
| FICA |  |  | 6.20percent |  | 6.20percent |  |  |
| MEDICARE |  |  | 1.45percent |  | 1.45percent |  |  |
| PENSION |  |  | 13.07percent |  | 0.00percent |  |  |
| TOTAL FRINGE BENEFIT RATE |  |  | 48.92percent |  | 13.35percent |  |  |
| Sick Pay Percentage Calculations |  |  |  |  |  |  |  |
| 8 hours per month x 12 months = 96 hours per year (96/1992 hours = 4.8percent) |  |  |  |  |  |  |  |
| Vacation Pay Percentage Calculations |  |  | In 1999 FEMA used 12 days. In 2004 the workforce will shift to 15 days on average due to the low turnover rate. (120/1992 hours per year = 6%) |  |  |  |  |
| 0-5 years of service = 10 days |  |  |  |  |  |  |  |
| 5-10 years of service = 12 days |  |  |  |  |  |  |  |
| 10-15 years of service = 15 days |  |  |  |  |  |  |  |
| 15-20 years of service = 17 days |  |  | Holiday Adjustment:. There are 9 observed holidays plus 2 additional holidays for a total of 11 (2,080hrs - 88hrs = 1,992hrs).. |  |  |  |  |
| 20+ years of service = 20 days |  |  |  |  |  |  |  |

### A7:  Forms for Loaning and Receiving Equipment

Loaning Agency Equipment Release Form

Use this form to:

- Document the loaning of equipment

- Authorize the loaning of equipment

INSTRUCTIONS:

Complete the form below and record the Loaner Agency’s Inventory Number, the Item Description and the Method of Delivery. Please use the comment section to provide additional information if needed. List the Receiver Agency’s delivery location and any special conditions for the equipment loaned.

I hereby accept the responsibility for and authorize the loan of the equipment listed below. The property has been inspected and has been identified with the following description.

_________________________/_______________ Authorized Loaning Agent

ID NUMBER		                 DESCRIPTION		                 	 CONDITION

COMMENTS: (hours, length and condition of loan etc)

____________________________________________________________________________________________________________________________________________________________________________________________________________________________

Details of Loan Agreement:

Facility Loaning Equipment: ________________________________________________________

Authorized Party of Loaned Equipment: _________________________________________________________

Physical and Mailing address of Loaned Equipment: _________________________________________________________________

__________________________________________________________________

Phone numbers of Loaned Equipment: _________________________________________________________

Receiver of Loaned Equipment: __________________________________________________________

Return / Delivery Method:

Receiving Agency Equipment Acceptance Form

Use this form to:

- Document the receiving of equipment

- Authorize the acceptance and responsibility of equipment

INSTRUCTIONS:

Complete the form below with the Receiving Facilities Inventory Number, the Item Description and the Method of Delivery. Please use the comment section to provide additional information if needed. List the receiver, location and agreed conditions for any property loaned

I hereby accept the responsibility of the equipment listed below. The property has been inspected and has been identified with the following description.

_________________________/_______________ Authorized Receiving Agent

ID NUMBER		                 DESCRIPTION		                 	 CONDITION

COMMENTS: (Fueling, hours, maintenance etc)

________________________________________________________________________________________________________________________________

Details of Loan Agreement:

Facility Receiving Equipment: ________________________________________________________

Authorized Party for Facility: _________________________________________________________ ____

Location of Loaned Equipment: _________________________________________________________

___________________________________________________________________

Contact Phone Numbers: ______________________________________________________________

Physical and Mailing address of Loaned Equipment: ___________________________________________________________________________________________________________________________________

Return / Delivery Method:

Staging and Set-Up Equipment Tracking Form

| ID Number | Equipment Description | Equipment Location | Contact Name | Phone Numbers | Comments |
| --- | --- | --- | --- | --- | --- |

### A8:  Sample Press Releases

#### City of Port St. Lucie Example Press Releases

- Precautionary Boil Water Notice

- News Release Lifting Precautionary Boil Water Notice

- Loss of Power to Wastewater Grinder Stations

- Conserving Water for Grinder Stations

- FAQ’s for Wastewater Grinder Stations

- Connection of Generators to Grinder Stations

- Status of W/WW Utility System

- Power Outages & Status of  W/WW Systems

- Emergency Public Water Access Locations

- Status of Water Storage Tanks

News Release: Precautionary Boil Water Notice

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 5, 2004     /     8:30 AM

Reissue:	September 6, 2004     /     7:30 AM

PORT ST. LUCIE --    	A precautionary boil water advisory is in effect for all customers of the City’s Utility.   The advisory will remain in effect until further notice.

News Release:  Lifting Precautionary Boil Water Notice

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 28, 2004     /    11:00  AM

PORT ST. LUCIE --    The boil water notice affecting all City of Port St. Lucie water customers has been lifted.

News Release:  Loss of Power to Wastewater Grinder Stations

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 5, 2004     /     8:49 AM

PORT ST. LUCIE --    	Power failures throughout the City will effect the operation of wastewater grinder and suburbanaire tank systems.

Therefore, all customers of the City’s Utility that are served by low-pressure sewer systems (grinder tanks and suburbanaire tanks) are still advised to conserve water use.  Customers should restrict all use of dishwashers and washing machines until further notice.  Do not take long showers.  Be conservative about toilet flushing.

News Release: Conserving Water for Grinder Stations

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 2, 2004

PORT ST. LUCIE --    	All customers of the City’s Utility that are served by low-pressure sewer systems (grinder tanks and suburbanaire tanks) are advised to conserve water use.  Customers should restrict the use of dishwashers, washing machines and long showers.

News Release: FAQ’s for Wastewater Grinder Stations

CONTACT:		Donna M. Rhoden, Utility Public Information Manager

Office:  772-873-6400    Fax:  772-873-6405

DATE:		September 24, 2004     /    10:30 AM

PORT ST. LUCIE --    	The following information is offered to our customers as before, during, and after storm or hurricane instructions.

1. 	Many of the City’s wastewater (sewer) customers are served by low-pressure Grinder Pump or STEP (septic tank effluent pump) systems.   What is a wastewater Grinder Pump or STEP system?

The system consists of a small electrical pump inside a fiberglass tank that is typically buried in the front yard of the customer’s property.

2.  	What happens when the Grinder Pump or STEP tank is full of wastewater?

The electrical pump will automatically run and the wastewater will be pumped through low-pressure sewer mains to one of the City’s three wastewater treatment plants.

3.  How much wastewater can an empty residential grinder tank

store?

Approximately 70 gallons.  Keep in mind that a toilet uses between 1.5 – 2.5 gallons of water each time it is flushed.

- What happens if there is a power failure such that a residence has no electricity?

If the electrical power is off, the Grinder or STEP system cannot operate.   Therefore, all Grinder and STEP system customers must conserve water usage until their electric power is restored.  They should flush toilets only when absolutely necessary and not take long showers.

5. What will the Utility do if a customer does not have electrical power to their Grinder or STEP system?

The Utility will make every effort possible to pump out or pump down a customer’s Grinder or STEP system when the storm or hurricane subsides.

6. Can customers connect their private generators to operate their   Grinder STEP systems?

Yes, but not until a City Utility employee instructs them on how to do it.  Also, the generator must be 220 Volt and it must be a minimum of 5,000 Watts.  Customers must provide their own "pigtail" (cord with plug).

7.  Is it safe to drink the City’s water after a hurricane?

A precautionary boil water advisory will be in effect immediately following the hurricane until such time as the City can assure the integrity of it’s water distribution system and the quality of water in its system.  If you are not able to boil the water, the St. Lucie County Health Dept. recommends that you add 8 drops of unscented household bleach per gallon of water, and then allow the water to sit for 30 minutes before consuming it.

8. Should the other City water and sewer customers do anything special after a hurricane?

Yes.  All customers of the City’s Utility are advised to conserve water use after the hurricane.  They should be especially conservative with toilet flushing, and they should not use dishwashers or washing machines.  Customers should not let water run for a long time in a sink or tub, and they should not take long showers.

9.  Utility customers should call 873-6400 if they have questions.

News Release: Connection of Generators to Grinder Stations

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 7, 2004     /     10:45 AM

PORT ST. LUCIE --    	Customers of the City’s Utility who have low pressure sewer grinder systems or STEP systems are requested to contact the Utility before they make any attempt to connect their personal electric generators to the City’s grinder or STEP pumps.  The Utility will dispatch one of its electricians to the site to instruct customers on how to make the connections.

Call:  873-6400

News Release: Status of W/WW Utility System

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 5, 2004     /     8:55 AM

PORT ST. LUCIE --    	Due to the continued presence of Hurricane Frances, the City’s Utility has been unable to deploy damage assessment and repair crews.  However, crews remain ready to activate and respond to system emergencies as soon as storm conditions subside.

News Release: Power Outages & Status of W/WW Systems

CONTACT:		City of Port St. Lucie Utilities

Donna M. Rhoden, Public Information Manager

Office:  772-873-6400  ¨  Cell:  772-528-2147

DATE:			September 5, 2004     /     8:45 PM

PORT ST. LUCIE --    	The City’s entire sewer system is down due to power failures throughout its utility service area.  The City is currently using all available generators to provide emergency power.  The delivery of additional generators is expected tomorrow to bring some relief until FPL can restore all power.

All customers of the City’s Utility are still advised to limit all water use.  Do not use dishwashers, washing machines, or take long showers, and flush toilets only as necessary.

News Release: Emergency Public Water Access Locations

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 5, 2004     /     8:15 PM

PORT ST. LUCIE --    	The City’s Utility Systems Department is in the process of establishing emergency water supply depots at the following locations:

1.  Church of God @t Savona / California

2.  Mobile gas station @ Gatlin / PSL Blvd.

3.  Shell gas station @ Tulip / Darwin

4.  Parkway Elementary @ Selvitz / Manville

5.  Publix @ Midport / PSL

6.  Publix @ Prima Vista Crossings at  U.S. #1 / Prima Vista

7.  Zapatas on U.S. #1 near Kitterman Rd.

Every attempt will be made to have all of the stations in service by 7:00 AM, Monday, Sept. 6th.

Residents must bring their own containers.  The boil water advisory will be in effect for each site.  Every attempt is being made to deploy adequate Utility staff so that each depot will be manned around the clock.

News Release: Status of Water Storage Tanks

FOR IMMEDIATE RELEASE:

CONTACT:		Donna M. Rhoden, Public Information Manager

Office:  772-873-6400    Cell:  772-528-2147

DATE:			September 3, 2004

PORT ST. LUCIE --    All of the City’s water storage tanks have been filled to maximum levels, thus providing a total of 9 million gallons of stored water that will be available to meet post hurricane demands.

### Lee County Utilities Hurricane Guide Tips

### Before the Hurricane

- Locate your residence’s emergency water shut-off valve and remove any shrubbery or obstructions.  Test the water shut-off valve to be sure that it is operational.  If the shut-off valve is not operational, have it repaired or replaced.

- Turn off the emergency water shut-off valve if you are leaving your residence prior to a storm.  This will help minimize damage to your home’s interior should a pipe burst inside the home.

- If you turn off the emergency shut-off valve, follow the manufacturer’s recommendations on turning off your hot water heater and unplug.  Some hot water heaters may be damaged if water supply is turned off for an extended period of time.

- Locate your sewer clean-out lid and remove any shrubbery or obstructions in case the clean-out needs to be located.

### After the Hurricane

- Due to power outages, water treatment plants will be operating under limiting conditions.  Water pressures will be reduced!

- Due to power outages, lift stations that are used to convey sewage to the wastewater treatment plants will not work or have only limited operations.  Over use of toilet flushing or water going down drains may cause lift stations to overflow and backup into your home.

Because of reduced pressures and limited operations of lift stations, WATER CONSERVATION IS A MUST!  Remember, just because power has been restored to your home, does not mean that power has been restored to all lift stations or water and wastewater treatment plants within your neighborhood.

- Limit the amount of toilet flushing.

- Abstain from running dishwashers and clothes washers.

- Limit the amount water used during a shower or the amount to fill the bathtub.

- Turn off all sprinklers!  Remember to reset your irrigation timer once power has been restored.

- Abstain from pressure washing, car washing, or any other outdoor use of water that is not necessary.

### Making Your Drinking Water Safe

During a storm event, trees can uproot water pipes allowing the underground pipes to be exposed to contaminated ground water or create a drop in pressure.  Once the storm passes, treat your water supply as if it is unsafe to drink until you are notified otherwise.  Boil water notices will be issued through your local Health Department and will be announced through your local Emergency Operations Center (EOC).

The use of bottled water should be used until bacteriological test prove that the water is safe to drink.  If you do not have bottle water here are ways to disinfect your water to make it safe.  Remember to disinfect any water being used for your pets.

Drinking Water

- Boil the water for at least ten minutes.

- If you do not have power and cannot boil your water, add eight (8) drops of unscented chlorine bleach per gallon of water.  Let the water sit uncapped for at least 10 minutes before drinking.

### Dish Washing

- Add fifteen (15) drops of unscented chlorine bleach per gallon to use for rinsing dishes.  Keep them clean until next use.

### Showering or Bathing

- Showering or bathing in tap water that is under a boil water notice is safe, if you cut yourself shaving use an antibiotic cream.

### A9: Sample Employee Assistance Plans

### City of Tamarac Summary of Employee Assistance after Hurricane Wilma

- On Wednesday, October 26, 2005, the City resumed operations notifying employees to return to work.

- Employees were provided special bulletins as often as appropriate to provide information regarding City operations.

- Meals including breakfast, lunch and dinner were made available for all employees working on hurricane recovery operations for two weeks.

- Employees were provided ice and water on a daily basis to take home.

- Employees were allowed to fill their gas tanks at the City’s fueling facilities so they could get to work without waiting in gas lines.

- Employees were paid on their regular payday schedules, and were offered the service of cashing personal checks through the City’s customer service office.

- Employees were provided contact information so they could communicate with FEMA, which had already declared Broward County eligible for individual assistance.

- Employees who had 457 Deferred Compensation accounts, and were affected by the hurricane were given the option of an emergency withdrawal of up to $5,000. This option was made available for 30 days, with a recommendation that all hurricane-related expense records be kept for IRS purposes. For those wishing to withdraw greater amounts, a representative was made available for assistance. Contact information was given and the option of a wire transfer of the funds was provided for those wishing to have the money routed to their accounts.

- The City County Credit Union offered emergency interest free 6 month loans to existing members of up to $1,000, as well.

- Operation Blue Roof was being implemented in Broward County, so City employees were given application pickup information and program updates with phone numbers, hours of operations, and projected contractor installations.

- Employees were provided information regarding the status of Broward County School closures.

- Employees were provided information regarding the status of traffic lights.

- Employees were provided information regarding Broward County Mass Transit free services.

- Employees were asked to assist other employees and to offer support to those impacted by the hurricane by contributing to cleanups, opening their homes for hot showers, telephone or cell phone calls, or for laundry.

- Due to anticipated bad weather, employees who experienced significant roof damage in their homes were provided roof tarps to protect their property.

- Employees whose homes were badly damaged and had to evacuate were offered temporary housing assistance.

- Employees were advised of price gouging and asked to keep their receipts and contact the police if they suspected price gouging. A help number was also offered for employees to contact in the event they experienced gouging.

- Emergency withdrawals from 457 Deferred Compensation accounts were made available from all carriers, and requests were typically being processed within 24-48 hours of the receipt of paperwork.

### A10: Boil Water Notice Guidelines

### A 13: Disinfecting Flooded Wells

### Applicability

If drinking water is obtained from a pubic well and you suspect that the well may have been contaminated, contact your local or state health department for specific advice

### Contamination Threats to Wells from Flooding

Flooding provides three pathways for contamination of a well, transport of contaminated water to the well head that can be present both above and below ground, surface inflow that passes directly into the well through openings at the ground surface and subsurface infiltration that enters the well by hydraulic actions caused by the well drawdown. The first flush of water from storm water facilities is often contaminated to an extent found in raw sewage. Flooding will transport these wastes directly to the well head.

Even if a well head has not been completely covered over with flood water, a poorly constructed well can become contaminated from surface water that enters through openings in the well or seeps in below ground. If you have had any standing water around a well head from a flood, then there is a good chance the well could be or could become contaminated.

Contamination can occur in both deep well and shallow wells and is not dependant on the volume of water or flow rate provided by the well. Contamination may be more dilute in a deeper, high-capacity well, but microorganisms could still affect human health.

The most common side affects of drinking contaminated well water is diarrhea. Diarrhea can be caused by a host of bacterial and viral pathogens and may occur after a few hours after drinking or being exposed to contaminated water to several days following exposure. It is not necessary to drink water to become ill when water is contaminated. Pathways for illness include from contaminated water on the hands to body openings in the eyes and mouth and from breathing aerosols that can enter the lungs. For this reason bathing or any other type of contact with contaminated water should be discouraged.

Fuel and other chemical releases and spills are common during flood events. If floodwaters water smells like fuel, has a chemical odor, or a sheen, contact your local or state health department to request a chemical analysis. Floodwater that carries fuels, solvents, pesticides or other chemicals can contaminate a well with constituents that will not be removed in the water treatment process. Until you know the chemical constituents that can be contaminating the water and their concentrations, the well may not be capable of producing water that is safe to use in the short-term.

### Safety Considerations for Cleaning and Disinfecting Wells

You will need to clear hazards away from well heads before attempting to clean and disinfect wells after floods and other natural disasters. The following precautions will help you do that safely:

Table 1

Safety Precautions for

Preparing a Well Head for Cleaning and Disinfection

- Before beginning any action, carefully inspect the area around the well for electrical and physical hazards. Those may include broken power lines on the ground or in the water; sharp metal, glass, or wood debris; open holes; and slippery conditions.

- Wear thick rubber-soled shoes or boots to protect against electrical shock.

- Turn off all power to the well area before clearing debris. Inspect all electrical connections for breaks in insulation and for moisture. Turn power back on only if all connections appear unbroken and dry with no opportunity for shock.

- Do not turn on any electrical equipment if there is a persistent smell of fuel such as gasoline coming from the well head. Allow the well to vent. If the smell persists, contact your local or state health department. Do not continue with disinfection of the well until the contamination in the well has been removed

- Before beginning work on the well, clear debris away from it to avoid inadvertently moving debris into the well.

Once the wellhead area has been safely prepared you can proceed to clean and disinfect the well. These additional precautions are recommended as you prepare to disinfect the well(s):

# Table 2

Additional Safety Precautions for

Preparing a Well for Cleaning and Disinfection

- The Chlorine solutions used to clean and disinfect a well can cause chemical burns. Use rubber gloves, protective eye wear, and waterproof aprons or rain gear when working with chlorine solutions.

- When mixing and handling chlorine solutions, work in well ventilated areas and avoid breathing vapors. When working in closed spaces, use electrical fans to provide fresh air. Exposures to chlorine fumes at high concentrations can damage lung tissue immediately and at low concentrations, exposure as low as 15 minutes duration can cause illness or injury.

- Warn users not to drink or bathe in water until all the well disinfection steps have been completed and the well has been thoroughly flushed.

### Cleaning and Disinfecting Wells Following a Flooded Condition

After following the above safety and health precautions the well is ready for cleaning and disinfection. The following procedures are recommended for cleaning and disinfecting wells that may have become contaminated by harmful microorganisms in floods or other natural disasters.

The disinfection process for a well can take from a few hours to a few days to complete. This process is recommended after floods and when a well has tested positive for coliform bacteria.

Chlorination is a process of flushing your well water system with a chlorine solution to inactivate pathogens. Chlorination is an effective method to inactivate microbial contamination, but if sampling shows that continual problems exist and they are linked to the well or groundwater from flooding, chlorination is only a temporary solution and will not protect the consumer of the water from microbial illness.

If the well contamination persists, further investigation is needed to determine the source of the problem. The procedures for well investigation are found in FAC 62-555.315 and 62-555.320.

If electrical power is not available at the well head, a portable generator may be needed to operate pumps and other equipment. Be familiar with generator operation found in other sections of this document before turning on a generator, energizing pumps, or any electrical equipment and have a qualified electrical technician make any electrical connections to prevent serious injury and damage to equipment..

After ensuring that safety procedures have been addressed, the well is ready for cleaning and disinfection. The recommended procedures follow:

Table 3

### Procedures for Cleaning and Disinfecting Wells

- Scrub and/or hose off foreign material from the well head, including the well slab, sanitary seal and pumping equipment. If the well seal was not properly installed and flooding has occurred, contaminated water, sand and silt may have been deposited in the well from this source, will be a contamination source and thus will need to be removed.

- Swab all top areas with chlorine solution. Since oil from street runoff may be contained in flood waters and is retained at the surface, it is recommended that a chlorine dose of 1,000 PPM be used for swabbing. This is about 2 ounces of bleach per gallon of water.

Contaminated flood water may also have entered the well through the well vent opening and/or electrical  conduits and these should be opened, cleaned and swabbed with chlorinated water and then flushed with clean water prior to attempting to disinfect the well. The amount of chlorine needed will be based on the type and extent of contamination.

- If flooding inundated the well head it may be impossible to remove all the debris deposited in the well. Special tools or pumps may be required to remove silt and sand that has settled to the bottom of the well. Heavy deposits of silt and sand may damage the well pump if not removed before the pump is started. If flooding resulted in a condition where considerable amounts of sand and silt were forced into the well, the pump column and well pump will have to be removed, any foreign substances removed and the well cleaned thoroughly before attempting disinfection.

- In instances of inundation, the well must be opened and all floating debris removed. The well should be purged by pumping until clear, to remove any suspended materials. The inside casing will require decontamination by swabbing from the surface the casing pipe to water level or if extremely deep, by repeated flushing from the top with strong non-foaming detergent such as Calgon or Trisocium Phosphate. If the well has been flooded, contaminated materials may have deposited on the sides of the casing and can be best removed by cleaning.

- The amount of chlorine to reach shock loading to be used to decontaminate a well will be determined from Table 5. These values are based on achieving a concentration of 50 PPM. For disinfecting a well that may have been contaminated, at least 200 PPM concentration of free chlorine residual must be maintained. If oil or high levels of organic matter have been washed into the well concentrations as high as 1000 PPM may be needed. This will also require the column and well pump to be removed and cleaned.

- If the pumping units are to be left in the well then these procedures should be followed. After purging well to clear condition, clean the casing with Calgon or Trisodium Phosphate by adding about 4 oz. to each gallon of water to be removed and cycling the well up and down several times. The gallons of mixture to be used is determined by the drawdown in the well.

- Chlorine solutions to be added to the well are determined from Table 6. How the chlorine solution is to be added is determined by whether the pumps are water or oil lubricated. If oil lubrication is used then chlorine must be added below the water well surface or it will be carried deep into the well. The solution should be added by lowering a hose into the well through the well vent if the pumps are oil lubricated.

This wash water is used to both flush deposits and oxidize any residue along the sides of the casing. The condition of the well can be visually observed by noting the condition of the lush water as it is removed. Empty spent rinse water from the well and repeat the process allowing the well to fill again.

- Add a chlorine solution to the well until it produces a free chlorine concentration as shown in Table 6. To determine free chlorine residual a DPD kit must be used. Cycle the well pump several times to get good chlorine distribution.

Table 5 provides recommended doses to reach acceptable free chlorination levels in the casing pipe. It is advisable to take a sample to determine that these levels are met or exceeded. Either unscented bleach liquid or solid chlorine can be used to disinfect a well.

To disinfect a contaminated well, shock chlorination is necessary. Shock chlorination cleans the well by oxidation and inactivates pathogens. The more contamination that is found or suspected the higher the dose of chlorine that needs to be used.

The highly chlorinated water must be held in the well for 24 hours before it is flushed out and the system is ready for testing. To determine the approximate amount of chlorine needed, find the corresponding well diameter in the left column of the table. Then match the amount of chlorine needed corresponding to the size of the well found on the right.

It is very important to determine the depth of your well. This information is typically recorded  in an O&M manual. If a the information is not available you will need to estimate the depth based on your best educated guess, then increase the suggested amounts of chlorine by 50%.

- The chlorine solution can be added trough the well vent or the air release valve may be removed if more diameter is needed. Once the solution is completely dispensed into the well it must be thoroughly mixed. This is accomplished by cycling the well pump on and off until a strong chlorine odor is persistent in the spent water. Drain to waste and do not pump contaminated water into any existing piping or pressure tanks. Disconnect piping between the pressure tank and pump if needed to allow contaminated water to flow away from the well and tank.

- Once the solution is thoroughly mixed the well is ready for disinfecting. Add additional makeup solution and then repeat this procedure several times at one hour intervals making sure that the required chlorine residual is maintained. Water pumped from the well should be clear and have a heavy chlorine odor.

- After several cycles stop the pump, note the time,  and allow the chlorine solution to remain in the well. The chlorine solution should be left in the well for 24 hours. Do not leave chlorine in the well for much longer than    24 hours because at high concentrations it can be corrosive to some pump parts.

- After the disinfectant has set in the well for the recommended period, turn on the pump and direct the water to a designated area away from the well. The water in the well contains high concentrations of chlorine that can be harmful to plants and aquatic life. Empty the water in an area where plants or streams will not be harmed. You should continue to pump the well until no chlorine odor is present.

- Confirm that there is no chlorine residual and take a bacteriological sample in accordance with DEP Standard Operating Procedures. Properly label, preserve and transport the sample to an approved laboratory for testing.

Table 4

Determining the amount of water inside

A Well Casing for Adding Detergent

| Well Diameter (inches) | Volume (gallons per foot ) |
| --- | --- |
| # 4 | # 0.65 |
| # 6 | # 1.47 |
| # 8 | # 2.61 |
| # 12 | # 5.88 |
| # 16 | # 10.44 |
| # 20 | # 16.30 |
| # 24 | # 23.50 |

# Table 5

Determining Chlorine Amounts

for Shock Chlorination (50 PPM) of a Well

| Laundry bleach (about 5.25% Hypochlorite) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Depth of water in well | Casing diameter |  |  |  |  |
|  | 4 inch | 6 inch | 8 inch | 10 inch | 12 inch |
| 10 feet | 1/2 cup | 1 cup | 1 1/2 cups | 1 pint | 2 pint |
| 25 | 1 cup | 1 pint | 2 pints | 3 pints | 4 1/2 pts |
| 50 | 1 pint | 1 quart | 2 quarts | 3 quarts | 1 gal |
| 100 | 1 quart | 2 quarts | 1 gal | 1 1/2 gal | 2 gal |
| 150 | 3 pints | 3 quarts | 1 1/2 gal | 2 gal | 3 gal |
| High-Test Hypochlorite (HTH 65-75% Hypochlorite) |  |  |  |  |  |
| Depth of water in well | Casing diameter |  |  |  |  |
|  | 4 inch | 6 inch | 8 inch | 10 inch | 12 inch |
| 10 feet | - | - | - | - | - |
| 25 | - | - | - | 1/4 lb | 1/2 lb |
| 50 | - | - | 1/3 lb | 1/2 lb | 3/4 lb |
| 100 | - | 1/3 lb | 3/4 lb | 1 lb | 1 1/2 lb |
| 150 | 1/4 lb | 1/2 lb | 1 lb | 1 1/2 lb | 4 lb |

# Table 6

# Factors to be Applied to Table 4 for Calculating Chlorine Concentrations for

Levels Greater than  (50 PPM) to Remove Organic Materials

|  | Observed Condition of The Well | Concentration of Chlorine Required for Disinfection | Minimum Factor to Use To Reach Desired Concentration |
| --- | --- | --- | --- |
| 1. | Loss of Power for extended period only, no flooding of Well Head has Occurred | 100 PPM | 2 |
| 2. | Any bacterial problems have been noted or expected and no flooding has occurred. | 200 PPM | 4 |
| 3. | Flooding is extensive in the area, standing water is observed and organic material may have reached Well Head through groundwater infiltration. | 300 PPM | 6 |
| 4. | Flooding is extensive and the well was been inundated or contaminated water has entered the well directly or organic material or oil has been identified in the well. | 1000 PPM | 20 |

Example:

From Table 6 a dose of 4 quarts of liquid chlorine bleach was determined to be necessary to Shock a Well. Standing water from floodwaters were observed standing near the well head. Water did not inundate the well and no organic material has been identified in the well.

From Table 5, a concentration of 300 PPM of chlorine is recommended to disinfect this well. The amount of chlorine needed is 6 X 4 quarts or 24 quarts (6 gallons of bleach.)  It is always preferable to use more chlorine than necessary if direct contamination is suspected.

Sampling Wells Following Cleaning and Disinfection

Until water has been tested and determined safe, any water for human consumption should be boiled (roiling boil for 1 minute), or an alternative water source used. Wait at least 2 days after disinfection to ensure that the chlorine has been thoroughly flushed from the system. Then sample the water for total coliform and either E. coli or fecal coliform bacteria to confirm that the water is safe to drink. Contact the local health department to have your water sampled and tested or contact your state laboratory certification officer to find a certified lab near you. You can also get this number from the U.S. Environmental Protection Agency’s Safe Drinking Water Hotline (800-426-4791 or www.epa.gov/safewater/labs/index.html).

If the sample results show no presence of both total coliform and E. coli or fecal coliforms, the water can be considered safe to drink from a microbial standpoint. Homeowners with private wells should follow up with two additional samples, one in the next 2 to 4 weeks and another in 3 to 4 months. To check the safety of your water over the long term, continue to monitor bacterial quality at least twice per year or more often if you suspect any changes in your water quality. Wells that serve Community Water Systems will need to meet the sampling requirements of the Florida Department of Environmental Regulation.

If sample results indicate the presence of total coliform and E. coli or fecal coliforms, repeat the well disinfection process and resample. If tests continue to show the presence of bacteria, contact your local health department for assistance.

### A14: Best Management Practices for Bacteriological Disinfection of Water Mains

### Adherence to AWWA Standard 651

Disinfection and Bacteriological Testing of Water Mains (local chlorination) is required for all pipe and fittings used to complete connections or repairs with the potable water system per AWWA Standard C651.

##### General Disinfection Procedures for Contaminated Water Main Repairs

- Water mains shall be prevented from contaminating materials during storage, installation and repair.

- Clear or flush any foreign materials that may have collected in the mains.

- Super-chlorinate water mains to disinfect any residual contamination.

- Flush super-chlorinated water from the water main.

- Protect the existing distribution system from contamination during the pressure tests and by super-chlorinated water.

- Initiate Bacteriological testing of water mains.

- Ensure that water main bacteriological quality meets DEP standards.

- Allow connection of disinfected water main to active distribution system.

### Use of Chlorine for Disinfection of Water Mains and Main Repairs

- Disinfection of Water mains is achieved using a chlorine solution to kill bacteria and other microorganisms after pipe installation and prior to testing. The disinfection process can take from a few hours to a few days to complete. Three (3) chlorination methods are acceptable to super-chlorinate water mains: Tablet, Continuous Feed, and Slug. The Tablet method gives a chlorine dose of approximately 25 mg/L; the Continuous Feed method gives a 24-hr chlorine residual of not less than 10 mg/L; and the Slug method gives a 3-hr exposure of not less than 50 mg/L free chlorine.

- The chlorinating agent and method of application shall be conducted in accordance with AWWA C651. Three Chlorination Methods are acceptable: 1.) the Tablet/Granular Method, 2.) the Continuous Feed Method and, 3.) the Slug Method. These described in the following sections:

# Tablet/Granular Method

- The tablet/granular method consists of placing Calcium Hypochlorite Granules or tablets in the water main as it is being installed and then filling the main with potable water when installation is complete. This method may be used only if the pipes and appurtenances are kept clean and dry during repair/construction.

- During pipe installation, Calcium Hypochlorite Granules shall be placed at the upstream end of each section of pipe and at the upstream end of each branch main.

- The quantity of granules used shall be as shown in Table 1, AWWA C651.

Table 1

Ounces of Calcium Hypochlorite Granules to be placed at the upstream end of each section of pipe and at the upstream end of each branch main at 500-ft Intervals

| Pipe Diameter | Calcium Hypochlorite Granules |
| --- | --- |
| 2-inches | 0.11 ounces |
| 4-inches | 0.5 ounces |
| 6-inches | 1.0 ounces |
| 8-inches | 2.0 ounces |
| 12-inches | 4.0 ounces |
| 16-inches and larger | 8.0 ounces |

- During construction, 5-gram Calcium Hypochlorite tablets shall be placed in each section of pipe. Also, one tablet shall be placed in each hydrant, hydrant branch, and other appurtenance.

Calcium Hypochlorite Tablets

| Pipe Diameter | 5 gram Calcium Hypochlorite Tablets per Pipe Segment |  |  |  |
| --- | --- | --- | --- | --- |
|  | 13-ft | 18-ft | 20-ft | 30-ft |
| 2-inches | - - - | - - - | - - - | - - - |
| 4-inches | 1 tablet | 1 tablet | 1 tablet | 1 tablet |
| 6-inches | 1 tablet | 1 tablet | 1 tablet | 2 tablets |
| 8-inches | 1 tablet | 2 tablets | 2 tablets | 3 tablets |
| 10-inches | 2 tablets | 3 tablets | 3 tablets | 4 tablets |
| 12-inches | 3 tablets | 4 tablets | 4 tablets | 6 tablets |
| 16-inches | 4 tablets | 6 tablets | 7 tablets | 10 tablets |

- Tablets shall be attached to the top of the pipe by a food-grade adhesive. The adhesive shall be only on the broadside of the tablet attached to the surface of the pipe.

- If the tablets are attached before the pipe section is placed in the trench, their position shall be marked on the section to indicate that the pipe has been installed with the tablets at the top.

- Filling and contact: Introduce water into the pipes at a velocity no greater that one (1) foot per second (fps).

- The chlorinated water shall be retained in the lines for a minimum of 24-hours. If the water temperature is less than 41o F (5oC), the water shall remain in the pipe at least 48 hours.

- Detectable chlorine residual of not less than 10 mg/l shall be found at each sampling point after the 24 hour, or 48 hour, period.

Continuous Feed Method

- The continuous-feed method of disinfecting water mains consists of completely filling the main to remove all air pockets, flushing the completed main to remove the particulates, and filling the main with potable water.

- Chlorinated water shall be introduced into the water lines at a point not more than 10 feet downstream from the beginning of the new main, water entering the new main shall receive a dose of chlorine fed at a constant rate such that the water will have not less than 25 mg/L free chlorine.

- The entire main shall be filled with the chlorine solution.

- Reference Table 4, AWWA C651 for required chlorine amounts.

- Prior to and during the disinfection process, valves shall be positioned so that the chlorine solution in the newly constructed main will not flow into water mains in active service.

- The chlorinated water shall be retained in the main for a minimum of 24-hours, at which time the treated water in all portions of the main shall have a free chlorine residual of not less than 10 mg/L.

- The water purveyor shall properly and legally dispose of flushing and super-chlorinated water.

# Slug Method

- The slug method consists of placing Calcium Hypochlorite granules in the main during construction, completely filling the main to eliminate all air pockets, flushing the main to remove particulates, and slowly flowing through the main a slug of water dosed with chlorine to a concentration of 100 mg/L

- Refer to Tablet / Granular Method for placing Calcium Hypochlorite granules.

- At a point not more than 10 feet downstream from the beginning of the new main, water entering the new main shall receive a dose of chlorine fed at a constant rate such that the water will not have less than 100 mg/L free chlorine.

- The chlorine shall be applied continuously and for a sufficient period to develop a solid column, or "slug" of chlorinated water that will, as it moves through the main, expose all interior surfaces to a concentration of approximately 100 mg/L.

- The free chlorine residual shall be measured in the slug as it moves through the main.

- If the free chlorine drops below 50 mg/L, the flow shall be stopped, chlorination equipment moved to the head of the slug, and as flow resumes, chlorine shall be applied to restore the free chlorine in the slug to not less than 100 mg/L.

- Flow rate shall be set so that all interior surfaces are exposed to a chlorine concentration of approximately 100 mg/L for a minimum of 3 hours.

### Flushing of Chlorinated Water Mains and Appurtenances

- After the applicable retention period is achieved for the chlorination method selected, the heavily chlorinated water shall be flushed from the water lines until chlorine measurement show that the concentration in the water leaving the main is no higher than that generally prevailing in the system, or less than 1 mg/L.

- The water purveyor shall be responsible for securing all necessary approvals from DOH/DEP or permits to ensure that no environmental damage occurs.

- Reference Appendix B of AWWA C651 supplies a list of neutralizing chemicals.

##### Ensuring Bacteriological Disinfection

- The water purveyor shall collect water samples to test for bacteriological quality to show the absence of coliform and heterotrophic organisms in the pipeline. Testing shall be done after final flushing and prior to pressure testing. Under no circumstances shall the main be pressure tested or put in service prior to bacteriological testing,

- Water mains shall not be placed in service until written release is obtained from DOH/DEP.

- The total coliform analyses shall be performed by a DOH approved laboratory.

- A total of at least two (2) samples each taken on a separate day and taken at least 6-hours apart from the other sample(s). The total chlorine residual must be no more than 4 mg/L.

- If any sample contains more than 4 mg/L total chlorine, the sample shall be considered invalid.

- If any sample shows the presence of total coliform, mains shall be re-disinfected and re-sampled until 2 consecutive samples at each sampling location show the absence of total coliform.

- Bacteriological test results shall be considered unacceptable if the tests were completed more than 60 days before the Department received the results. In Emergency situations, bacteriological tests may be returned within 24 hours.

- No treatment facility, storage tank or water mains shall be placed into service until a bacteriological evaluation has been satisfactorily completed, results of the evaluation have been submitted to the appropriate DEP District Office or Approved County Health Department, and APPROVED the facilities or mains for operation.

- A Water System may be approved to allow a water main to supply water to be used for public consumption on the basis of the first confirmed negative test. This will require concurrence of DOH/DEP. The second consecutive sampling must proceed and also show a confirmed negative result. If the test is positive, the procedures described here must be repeated.

- If the initial disinfection, or subsequent disinfections, fail to produce satisfactory samples, the main shall be re-flushed and re-sampled. If the samples are still not satisfactory, the main shall be re-chlorinated by the continuous-feed or the slug method of chlorination until satisfactory results are obtained.

### A 14: Restoring Electric Motors Flooded by Saltwater

by Robert McVay P.E., Florida Rural Water Association

### Introduction

According to the Electrical Apparatus Service Association, even motors submerged in salt water may be restored if properly cleaned, dried and tested. Flooded motors and transformers were sent to motor repair shops all over the U.S. and successfully restored to serviceability following Hurricane Katrina. Lessons learned here can be applied to future hurricane flooding events. Some simple steps will help those involved in hurricane restoration activities to increase the probability of success for a motor repair following saltwater flooding.

### Before the Flood

There are not a lot of ways to minimize flood damages to motor drive systems, but keeping critical systems on higher ground is the best way to protect them. Here are some suggestions to help prepare for large or small equipment saltwater damage.

Table 1

Minimizing the Affects of

# Saltwater Flooding of Electrical Equipment

- Track motor inventory and identify in advance which motors are candidates for replacement if they become compromised. Be sure to back up these records in an off-site location.

- Multi-facility companies should store some critical spare parts at various facilities so they will survive a disaster that hits one facility.

- Determine if company service centers have a plan for restoring a large volume of flooded motors.

- Invest in a predictive maintenance program for motors and transformers, including diagnostic equipment that assesses insulation integrity. This will provide baseline information on insulation condition and identify problem equipment that needs rewinding or replacement. It can also help improve equipment reliability even in dry times.

### Minimizing Insulation Damage to Electric Motors

Seawater has a total dissolved-solids concentration of about 35,000 mg/L, of which dissolved chloride is the largest component (about 19,000 mg/L). Concentrations of chloride in fresh ground water along the Atlantic coast are typically less than about 20 mg/L, so there is a large contrast in chloride concentrations between freshwater and saltwater. Motors that have been flooded by freshwater are typically very repairable. However, saltwater flooding poses a more significant threat to a flooded motor because of the conductance of the minerals that are present. The critical step in restoring an electric motor that has been flooded by salt water is to keep the windings flooded, or at least wet, until they can be flushed using clean fresh water. If salt water dries in a winding, it becomes almost impossible to dissolve and remove the mineral deposits by flushing. If service centers are backed up for weeks, major industrial facilities may be able to set up temporary "field hospitals" for flooded motors. However, this work needs to be at least supervised, if not performed, by trained electrical equipment service personnel.

### Planning for Saltwater Damages to Motors and Electrical Equipment

Storm surges and resultant coastal flooding from hurricanes can reach several miles inland submerging electrical equipment including motors. Direct replacement of electric motors can take several weeks or longer rendering critical facilities inoperative. The overload of motor repair facilities and demands for critical repair equipment can likewise be extremely lengthy if hurricane damages caused by storm surges along the coastline are extensive. For this reason utilities are advised to review rehabilitative procedures that can return electric motors to operating status in less than 24 hours.

Utilities in coastal areas are advised to review the special rehabilitation procedures for saltwater submerged motors. These procedures are different than those typically used for freshwater flooding. Failure to adhere to these best management practices may result in irreversible damage to motors.

Coastal utilities are advised to develop operating agreements with local and regional electrical motor repair shops to ensure that the facilities are equipped to handle the extra workloads that are possible with coastal flooding and that personnel in these shops understand the rational and the special procedures that are necessary to rehabilitate electrical equipment submerged in saltwater.

### Procedures for Flushing Saltwater from Motor Windings

Floods will carry dirt, sand, sediment, and other foreign materials that will lodge in all parts of the motor, particularly the windings. This material can be removed using a hose with water on

low pressure, or flushing directly with fresh water until removed. Saltwater however, can not be removed with simple flushing since any mineral deposits remaining on motor surfaces will be hydroscopic and eventually lead to oxidation of metal or shorting of insulation leading to motor failure. Mineral deposits will also chemically react with insulation causing it to deteriorate.

Never attempt to restart an electric motor that has been flooded. It may permanently damage the device. The motor may be damaged internally or contain moisture that could cause electrical shock.

Saltwater is particularly problematic to motor windings and procedure have been developed that can be successful if employed quickly. These procedures provide excellent results for removal of saltwater deposits from windings if the surfaces have remained wet or if the surfaces have remained flooded with saltwater and have not dried out. The procedure will likely not be successful if the windings have been allowed to dry. The sooner the procedure is initiated after saltwater flooding the better the results will be.

The table below illustrates the preferred technique for addressing saltwater flooding of motors.

Table 2

Procedures for Restoring Electric Motors

Flooded by Saltwater

- Keep motor windings submerged in water; fresh water is preferable but if only saltwater is available keep the windings flooded; Do not allow the motor to dry!

- Transport Motor as soon as possible to an electric motor repair shop

- The motor must be disassembled and mud, silt and deposits removed by flushing with water using a hose not to exceed a pressure of 25 psi. Tight adhering deposits will require agitation or gentle brushing or wiping. A mild non-conductive detergent diluted to 1 pint to each gallon of water, is sometimes used to aid in the cleaning process.

- After motor parts have been thoroughly cleaned they must flushed to remove mineral deposits caused by the saltwater.

- Immerse motor parts for 8 hours in fresh water

- Water must be turbulent/agitated continuously in the tank

- Water must be continuously exchanged at a rate of 20-50 gpm

- After the procedure is completed the motor parts should be wiped with a clean cloth, grease and oil replaced in bearings and metal surfaces and the motor parts reassembled for drying

# Construction of Motor Flushing Container

Most motor repair shops will not have the flushing equipment described above that is essential for removal of saltwater deposits. The following information is provided for constructing such a device.

After a strong hurricane, tidal surges can inundate a significant number of electric motors and a large flushing device can accommodate several motors at one time. A dumpster or similar sized container can be quickly constructed to serve this purpose.

Construction of a Saltwater Flush Box  (See figure below)

### Water Inlet and Flushing Pipe

Route a 3/4” or larger pipe in from the top of the tank down to the bottom, then route pipe along the length of the bottom of the tank down to the bottom, then route pipe along the length of the bottom of the tank, roughly centered. Cap the other end of that pipe, drill holes at a slight upwards angle along both sides of pipe. This pipe serves as the water jets. Size holes appropriate for the available water pressure, no more than 1/8" diameter. The more holes, the smaller they will have to be. The holes will serve as water jets to ensure adequate agitation and flushing and to direct water toward motor parts and prevent short circuiting.

### Constructing the Drain

A hole should be drilled near the top, opposite of the inlet, to allow water to be drained from the container. A nipple or sealed threaded pipe can be used to retain water tightness and serve as a connection for directing water to a suitable drain.

Flush Box for Saltwater Mineral Deposit Removal

Load tank with motor stators, fill with clean fresh water, and operate for 8 hours.

Remove, pressure wash, and bake stators. Drying times of windings that have been immersed require longer drying times. A good estimate is to bake coil windings twice as long as normal for the size motor that is being repaired.

### Procedures for Drying Motors After Flushing

Motor windings must be thoroughly dry before the motor can be started. If windings are not thoroughly dry, the motor may short circuit when electricity is turned on. Drying can be accomplished with a controlled temperature oven, heat lamps over the motors, running DC voltage through the windings or make-shift tunnels directing heat to the motor a propane heater. Preferred baking methods are described below:

Table

Acceptable Methods for Drying

Saltwater Flooded Motors

- Baking is accomplished by use of a circulating-air oven at a temperature not to exceed 90oC (194o F) until the insulation resistance becomes practically constant.

- Enclose the motor with canvas or similar covering , leaving a hole at the top for moisture to escape and insert heater or heat lamps.

- Pass a DC current at 10% of the rated motor voltage (with rotor locked) through the stator windings and gradually increase the current until the winding temperature reaches 90oC (194o F). This temperature should not be exceeded.

A minimum of 8 hours drying time should be used for saltwater flooded and freshwater flushed motor. If windings are firm and stiff after 8 hours, drying is complete, if not, more drying time is necessary.

##### Directions for the Construction of a Drying Oven for Multiple Motors

In an emergency situation, there may be a large number of motors to dry. In this case the drying oven will be inadequate to accommodate the larger number of motors. In this case a field expedient oven can be constructed to expedite the work.

Construction of Drying Oven (see figure below)

#### Oven Construction

Energy-shield, the hard-sided-foam insulation available at building supply stores can be effectively used to construct drying ovens to accommodate large numbers of motors. This material has a layer of aluminum foil on both sides and has exceptionally good insulating value (R-29) for its thickness. The sheets are lightweight, easy to handle and cut with a knife. They are also reusable.

For motors with very large frames, box the motor by placing energy-shield directly on the frame, including the top. Seal the oven joints with aluminum duct-tape.

Place the energy-shield directly on the fame to minimize the volume of air that must be heated. This also reduces drying time because the insulation minimizes heat loss.

###### Recommended Drying Oven Heat Sources

The most effective heat source is a torpedo propane fueled blower. The blower should be situated so it blows hot air directly into the center of the motor bore. The sizing of the blower should provide 100,000 BTU per 1200 cubic feet of oven volume.

###### Control of Oven Temperature Gradients

For accurate measurement of motor winding temperatures direcly monitor the motor’s RTDs. If RTDs are not available a infrared thermometer or other heat sensing devices can be used to monitor temperature in various parts of the oven. The key is to keep the heat uniform within the motor.

Dampers should be constructed on the oven at the four corners as shown below. Dampers allow the temperature in the oven to be adjusted in various locations within the oven and allow a more uniform heat distribution. An increased flow of hot air through an area can be accomplished by opening a particular damper. Regulating temperature with dampers is more effective than using a tarp or supplying current to windings.

###### Determining Adequate Drying Time

Drying time should be a minimum of 8 hours and can be determined with the use of a voltage meter. The iron frame and copper windings of a motor act as two plates of a crude battery. Electrolytic action across the wet insulation causes current to flow. If voltage flow is detected then moisture is present. When voltage drops to zero, the windings are dry. If voltage is present the drying process must be extended.

Oven for Drying

Saltwater Flushed Motors

### Motor Insulation Resistance Testing

The primary purpose of a motor insulation resistance test is to determine if the motor can be placed back into operation. If resistance to ground is not acceptable, the motor is likely damaged and must be rewound.

IEEE Standard 43-200,  “Recommended Practice for Testing Insulation Resistance of Rotating Machinery is governs acceptable resistance limits for motor windings for placing a motor back into service. The standard serves two purposes: 1.) provides a quantitative evaluation for placing the motor in service and 2.) provides a baseline for monitoring to determine over the long-term if the repair has been completely successful.

The basis of the test is to determine a resistance value (IR.) If the IR value is value is below the accepted IEEE Standard 43-200 minimum, the motor can be placed in service. The IR value in the table will be taken under an applied voltage condition for a period of 1 minute. The 1 minute holding time allows capacitive effects to stabilize giving more accurate results.

The most commonly used device for making IR readings is the 500 volt battery-powered DC megohmmeter. One lead is applied to the winding leads (typically each phase measured individually by connecting them to the instrument lead) and the other instrument lead is connected to the frame of the motor (ground.) Test voltage applied increases with the machines voltage rating. The test should be conducted at 40oC (104oF).  The meter will display the winding megohm value (IR). The table below provides the acceptable ranges for the motor rated voltage.  For most water and wastewater motors the voltage requirement will be 480 volts and below thus a test voltage of 500 V is required.

### Interpreting Motor Condition Using IR Readings

IR readings taken from a megohmmeter must be corrected for temperature. Temperature corrections are shown below: An example for use of the chart is shown on the right.

Given: 240V, 3 Phase Motor

Motor Manufactured 1985

IR Value at 30oC = 15.3 M

IR Value at 40oC

IR Value Correction Factor from  Chart = 0.5

IR = 15.3 MX 0.5

IR = 7.65 M

For this particular motor manufactured after 1985, the required minimum resistance is taken from the above table at greater than 5 megohm and the IR value is 7.65 M thus the motor can be placed in operation. Should the IR value be below 5 megohm the motor could not be placed in operation.

### Polarization Index (PI) Test

The purpose of the PI test is to determine the condition of the insulation. The PI test measures the leakage current change in a winding that is an indication of its integrity of the insulation and its ability to function long-term. The test is run over a 10 minute period with a constant test voltage applied. PI is the ratio of the IR at 10 minutes to the IR value at 1 minute. The PI value must be 2 or higher for a motor to be placed back in service.

In some cases, the additional motor drying may increase the PI value. A PI that can not be corrected would indicate that the windings are permanently damaged and the motor must be rewound.

### Precautions in Interpreting Motor Megohm Test Results

Many factors such as humidity, temperature, accuracy and sensitivity of the equipment used and the capacitance properties of an electric motor can contribute to false readings.

Failure to recognize capacitance is a common error is performing electrical testing of motors. Capacitance problems can be minimized by connecting all circuits that are not being tested to ground.

If solvents have been used in the cleaning process, voltages applied during the testing can cause arcs that can ignite and cause explosions.

In all cases electrical integrity testing of motors and electric equipment should be performed by a skilled electrical repair specialist.

### Lubrication Considerations for Saltwater Flooded Motors

Lubrication serves two functions in an electric motor, these are to lubricate contact surfaces and to prevent corrosion. Saltwater contains corrosive minerals that will hasten the breakdown of lubricants, cause oxidation and accelerate and contribute to the corrosion of metal surfaces. Thus it is recommended that all bearings be replaced if possible or if parts are not available, that all parts be purged of saltwater residue and contact surfaces be lubricated. This will require flushing parts in a warm agitated solvent bath to remove both contaminants and old oil and grease. In general, bearings should be replaced if flooded with saltwater and only reused if no other alternative available. Thus it is important to stock adequate supplies of spare parts.

Bearings should not be reused if there is evidence of wear, edge loading, fatigue embedment scoring, or lack of clearance, journal damage or other obvious problems during disassembly.

It is beyond the scope of this BMP to describe all of the requirements for proper rebuilding of a motor and a skilled technician experienced in motor rebuilds should always be employed for this purpose or much time and effort in reversing saltwater damage will have been wasted.

### References

Procedures for Flushing Saltwater From Windings

Chuck Yung, EASA Technical Support Specialist, EASA,  2005

Field Expedient Ovens

Chuck Yung, EASA Technical Support Specialist, EASA, 2005

Insulation Resistance Testing: How Low Can Megohms Go

Tim Bishop, EASA Technical Support Specialist, EASA, 2005

Maintenance Engineering Handbook, Sixth Edition

Lindsey R Higgins PE and L.C. Morrow. McGraw Hill, 2001

The Disaster Handbook 1998 National Edition

Institute of Food and Agricultural Sciences, University of Florida